## Main
WAREHOUSE VENTILATION CALCULATIONS
PROJECT | MY PROJECT NAME
BUILDING | MY BUILDING NAME
DATE | 2015-06-19 10:44
by | MY NAME HERE
INPUT
BUILDING
FLOOR AREA | 500000 | SQ. FT.
BLDG HEIGHT | 40 | FT.
PRODUCT VOLUME | 50% | (assumed warehouse volume occupied by product)
FORKLIFTS | 0 | (number of propane forklifts operating)
VENTILATION
AIR CHANGES | 3 | PER HOUR
% POSITIVE | 5% | (percent positive pressure)
CODE CFM/SF | 0.05 | (0.05 CFM/SF for IMC & FL; 0.06 CFM/SF for CA & ASHRAE 62)
Note: LEED EQ Pre 1 requires ASHRAE 62 rate 0.06 CFM/SF
CALCULATIONS
EXHAUST FANS
|  | ( | 500000 |  |  |  | x | 40 |  | ) | x | 50% | x | 3
60
|  | = |  | 500000 |  |  |  |  | CFM EXHAUST FAN TOTAL
SUPPLY FANS
|  | 105% |  |  | x | 500000
|  | = |  | 525000 |  |  |  |  | CFM SUPPLY FAN TOTAL | [5 empty] | VENTILATION | VENTILATION | VENTILATION
[15 empty] | BASED ON | BASED ON | BASED ON
[15 empty] | AIR-CHANGES PER HOUR | FORKTRUCKS | MIN CFM/SQ. FT.
MINIMUM (WINTER) VENTILATION REQUIREMENTS
| 500000 |  | SQ. FT. x 0.05 CFM/SQ. FT
[15 empty] | 500000 | 0 | 25000
|  | = |  | 25000 |  |  |  |  | CFM MIN VENTILATION REQ'D
Copyright © Mike Ballew